## Heat Calcs - 1st HE
Manual Input
Calculated Output
Heat Input
[11 empty] | Minimum | Nominal | Maximum
Clear Preg mass flow rate |  |  | 15 | m3/hr |  |  | Clear Preg mass flow rate |  |  | m3/hr | 10 | 12.5 | 15
|  |  | 4.375 | kg/s |  |  | Temperature In |  |  | ºC | 80 | 80 | 80
Clear Preg density |  |  | 1050 | kg/m3 |  |  | Temperature Out |  |  | ºC | 50 | 50 | 45
Specific heat of clear preg |  |  | 4.198 | kJ/kg K
T 1 |  |  | 80 | ºC | temperature in |  | Cooling Water mass flow rate |  |  | m3/hr | 11 | 27.6 | 58
T 2 |  |  | 45 | ºC | required temp out |  | Temperature In |  |  | ºC | 20 | 35 | 35
|  |  | 598.4448 | kW |  |  | Temperature Out |  |  | ºC | 50 | 50 | 45
Cooling Source | [6 empty] | Heat removal requirement |  |  | kW | 385 | 481 | 673
Cooling water flow rate |  |  | 51.5407 | m3/hr
|  |  | 14.3169 | kg/s
Cooling water density |  |  | 1000 | kg/m3
Specific heat of CW |  |  | 4.18 | kJ/kg K
T1 |  |  | 35 | ºC | ambient temperature
T2 |  |  | 45 | ºC
Heat input = Cooling source |  |  | (mass)*(specific heat)(delta T)
598.4448 | kW | = | Cooling Source kW
|  | = | kg/ s * Cp * (delta T)
|  | = | 41.8 | kg/s
|  | = | 14.3169 | kg/s
* Assumption is 100% efficiency, which is not true
Amsul solution Cp
Amsul | [5 empty] | Amsul solution estimate
Temperature | 25 | °C
| 298 | K |  |  |  | Amsul solid added |  | 1000 | kg
cp Amsul | a | 103.554 | = | 187.2163 | J/molK | Volume of ater added to mixing tank |  |  |  | 10 | m3 | 10000
| b | 0.28075 |  |  |  | Density of raw water |  |  |  | 1 | g/cm3 | 1
| c | 0 |  |  |  | Mass of raw water in mixing tank |  |  |  | 10000 | kg
| d | 0
[6 empty] | Mass fraction Amsul |  |  | 0.090909
[6 empty] | Mass fraction raw water |  |  | 0.90909
Water |  |  | MW | 18.012
Temperature | 25 | °C |  |  |  | Cp Amsul solution estimate |  |  | 85.8932 | J/molK
| 298 | K
cp Water | a | 20.36 | = | 75.7609 | J/molK
| b | 0.1092
| c | 2030000
| d | 0
Sodium vanadate solution estimate
Vanadate solution Cp
[6 empty] | Clear Preg |  | 55 | g/L (V)
Sodium vanadate |  |  | MW | 121.93 |  |  |  | 1.0797 | mol/L (V)
Temperature | 25 | °C
| 298 | K |  |  |  | Assuming all V from vanadate
cp Amsul | a | 255.391 | = | 195.0681 | J/molK | mol vanadate |  | 1.0797 | mol/L
| b | 0.006276 |  |  |  | mass vanadate |  | 131.6441 | g/L
| c | -5523000
| d | 0 |  |  |  | Density of Barren solution |  |  | 1.02 | g/cm3 | 1020 | g/L
[6 empty] | Mass fraction vanadate |  |  | 0.11431
[6 empty] | Mass fraction Barren |  |  | 0.88569
[6 empty] | Cp Vanadate solution estimate |  |  |  | 89.3989 | J/molK
Note on D9: flormirza.cabalteja: assumption only, specific heat of water at 90ºC
Note on E58: flormirza.cabalteja: previously 183.908

## Flow and Heat Calcs - Precip
| Manual Input |  |  | Linked Value
Calculated Output
Test | Recycle length | Recycle Flow |  | Recirculating Load | Residence Time in Tank | Diameter | A | Q | Velocity of Recycle Flow | Retention time of recycle in line | Re | Temperature | Dynamic Viscosity | Kinematic Viscosity
| (m) | L/min | m3/hr | % of Tank Volume | hr | mm | m2 | m3/s | m/s | s |  | - t - | - µ - | - ν -
[9 empty] | ~1.5-2m/s | >60s | > 4000 | (oC) | (N s/m2) x 10-3 | (m2/s) x 10-6
1 | 10 | 475 | 28.5 | 33.9286 | 5.6 | 100 | 0.00785 | 0.0079167 | 1.0085 | 9.9158 | 100647.961 | 0 | 1.787 | 1.787
2 | 10 | 550 | 33 | 39.2857 | 5.6 | 100 | 0.00785 | 0.0091667 | 1.1677 | 8.5636 | 116539.7443 | 5 | 1.519 | 1.519
3 | 10 | 650 | 39 | 46.4286 | 5.6 | 100 | 0.00785 | 0.010833 | 1.38 | 7.2462 | 137728.7887 | 10 | 1.307 | 1.307
4 | 10 | 750 | 45 | 53.5714 | 5.6 | 100 | 0.00785 | 0.0125 | 1.5924 | 6.28 | 158917.8331 | 20 | 1.002 | 1.004
5 | 10 | 850 | 51 | 60.7143 | 5.6 | 100 | 0.00785 | 0.014167 | 1.8047 | 5.5412 | 180106.8775 | 30 | 0.798 | 0.801
[12 empty] | 40 | 0.653 | 0.658
Precipitation Tank Volume |  |  | 95.3736 | m3 | [7 empty] | 50 | 0.547 | 0.553
| (based on inv calcs) |  | 84 | m3 | [7 empty] | 60 | 0.467 | 0.475
| D |  | 4.7 | m | [7 empty] | 70 | 0.404 | 0.413
| Working H |  | 5.5 | m | [7 empty] | 80 | 0.355 | 0.365
[12 empty] | 90 | 0.315 | 0.326
Clear Preg Flow Rate |  |  | 10 | m3/hr | [7 empty] | 100 | 0.282 | 0.294
|  |  | 12.5 | m3/hr
|  |  | 15 | m3/hr | [7 empty] | 1 N s/m2 = 1 Pa s = 10 poise = 1,000 milliPa s
1 m2/s = 1 x 104 cm2/s =1 x 104 stokes = 1 x 106 centistokes
Precip Tank 1 Heat Removal Requirement
Heat Input
Recycle Flow Rate |  |  | 28.5 | m3/hr
|  |  | 8.3125 | kg/s
Recycle Flow Density |  |  | 1050 | kg/m3
Specific Heat of Recycle Flow |  |  | 4.198 | Cp
T 1 |  |  | 45 | ºC | temperature in
T 2 |  |  | 40 | ºC | required temp out
|  |  | 174.4794 | kW
Cooling Source
Cooling water flow rate |  |  | 15.0269 | m3/hr
|  |  | 4.1741 | kg/s
Cooling water density |  |  | 1000 | kg/m3
Specific heat of CW |  |  | 4.18 | Cp
T1 |  |  | 30 | ºC | ambient temperature
T2 |  |  | 40 | ºC
Heat input = Cooling source
174.4794 | kW | = | Cooling Source kW
|  | = | kg/ s * Cp * (delta T)
|  | = | 41.8 | kg/s
|  | = | 4.1741 | kg/s
Precip Tank 2 Heat Removal Requirement
Heat Input
Recycle Flow Rate |  |  | 28.5 | m3/hr
|  |  | 9.1042 | kg/s
Recycle Flow Density |  |  | 1150 | kg/m3
Specific Heat of Recycle Flow |  |  | 4.198 | Cp
T 1 |  |  | 40 | ºC | temperature in
T 2 |  |  | 35 | ºC | required temp out
|  |  | 191.0965 | kW
Cooling Source
Cooling water flow rate |  |  | 32.9161 | m3/hr
|  |  | 9.1434 | kg/s
Cooling water density |  |  | 1000 | kg/m3
Specific heat of CW |  |  | 4.18 | Cp
T1 |  |  | 30 | ºC | ambient temperature
T2 |  |  | 35 | ºC
Heat input = Cooling source
191.0965 | kW | = | Cooling Source kW
|  | = | kg/ s * Cp * (delta T)
|  | = | 20.9 | kg/s
|  | = | 9.1434 | kg/s
Note on L4: Flormirza Cabalteja: density x velocity x D / dynamic viscosity values calculated are similar to online Re calculator (http://www.efunda.com/formulae/fluids/calc_reynolds.cfm#calc)
Note on D27: flormirza.cabalteja: Use Precip 1 density
Note on D28: flormirza.cabalteja: assumption only, specific heat of water at 90ºC
Note on D52: flormirza.cabalteja: Use Precip 2 density
Note on D53: flormirza.cabalteja: assumption only, specific heat of water at 90ºC